## Sheet1
Yang et. al | Reddy et. al | Pedrini et. al | ASHRAE sample checklist for hourly simulation (https://www.ashrae.org/technical-resources/bookstore/procedures-for-commercial-building-energy-audits) | Silva et. al
Chiller COP | Lighting schedule | Cooling setpoint schedule | Weather file/zone | Solar absorptance roof
Wind speed | Equipment schedule | Fan coil schedule | Correct site altitude | Solar absorptance wall
Occupant activity | Auxiliary equipment schedule | Occupancy schedule | Ground reflectance | Ground reflectance
Heating/Cooling schedule | Fans schedule | Lighting power density | Utility rates schedule | Specific heat of wall
Chilled water delta T | Space heating temperature schedule | Equipment power density | Walls, windows, floors, underground floor constructions per drawing | Ground temperatures
Solar absorptance | Space cooling temperature schedule | Lighting schedule | Constructions per drawing | Thickness of the wall
Material Conductivity | Outside air ventilation schedule | Equipment schedule | Window and frame properties (check correct treatment of outdoor air coefficient) | Emissivity of the roof
Occupancy schedule | Window shading coefficient |  | Slab heat transfer coefficients | Specific heat of the concrete
Lighting fraction radiant | Window uvalue |  | Building floor area | Density of the wall
Surface albedo | Wall uvalue |  | Skylights if needed | Ventilation opening area
Fan total efficiency | Lighting power density |  | Include window overhangs where needed | Thermal conductivity of the floor
Light schedule | Equipment power density |  | Include exterior shading from other parts of building | Number of occupants
Temperature sensor height | Supply fan power/delta T |  | Include exterior shading from other buildings | Average power of equipment
Occupancy time interval | Energy efficiency ratio |  | Equipment internal load density | Schedules of occupancy
Solar heat gain coefficient | On hours control |  | Equipment schedules | Availability schedule of operation of doors
Hot water sizing factor | Off hours control |  | Lighting load density | Radiant factor of equipment
Wall ufactor | Minimum supply air flow |  | Lighting schedules
Equipment/appliance schedule | Economizer |  | Occupancy number
Average ventilation rate change | Minimum outside air |  | Occupancy schedules
Chiller part load | Auxiliary electrical loads – Non-HVAC effect |  | Infiltration loads (air changes/hour or flow per unit area)
Boiler efficiency | Cooling tower fan power |  | Verify infiltration schedules
Heating/cooling time interval | Cooling tower fan control |  | Add daylighting controls as appropriate
Occupant heat load | Primary CHW and condition pump flow |  | Zones are consistent with building construction
AHU minimum airflow rate | Boiler efficiency ratio |  | Zone thermostat setpoints and schedules
Heat recovery efficiency |  |  | Outdoor airflow/person in zones
Fresh air introduction rate |  |  | Assign zones to correct systems and specify control zone as appropriate
Maximum zone wind speed |  |  | Verify equipment operating schedules
Minimum outside air fraction |  |  | Size systems
Airflow convergence tolerance |  |  | Size heating coil capacities
Lighting time interval |  |  | Size cooling coil capacities
Ground temperature |  |  | Exhaust fans and controls as needed
Minimum surface convection heat transfer coefficient |  |  | Ensure fans and controls as needed
Ground reflectance |  |  | Ensure fan energy and compressor power are separate (packaged units)
Reference barometric pressure |  |  | Verify supply air setpoints and resets
Specify configuration of hot-water, condense-water, and chilled water loops
Verify equipment operating schedules, capacities, and part-load efficiencies
Boilers (if multiple, ensure correct staging)
Chillers (if multiple, ensure correct staging)
Pumps, (if multiple, ensure correct staging)
Verify equipment control sequences
Check pump definitions use (1) kW input or (2) flow rate, pressure drop, and efficiency (not both)

## Sheet3
Levels
| CONTINUOUS PARAMETERS | Lower | Base | Upper | Basis for best guess values | 0 | 0.3333 | 0.66667 | 1
X1 | Concrete thermal absorptance | 0.001 | 0.9 | 0.999 |  | 0 | 1/3 | 2/3 | 1 | What I need is a sensitivity analysis tool that is not costly to compute and has the ability to provide rankings (qualitatively or quantitatively) of the importance of the input parameters to the output
X2 | Concrete solar absorptance | 0 | 0.7 | 1 |  | 0 | 1/3 | 2/3 | 1
X3 | Plywood thermal absorptance | 0.001 | 0.9 | 0.999 |  | 0 | 1/3 | 2/3 | 1
X4 | Plywood solar absorptance | 0 | 0.7 | 1 |  | 0 | 1/3 | 2/3 | 1
X5 | Air gap thermal resistance | 0.001 | 0.18 | 1 |  | 0 | 1/3 | 2/3 | 1
X6 | People fraction radiant | 0 | 0.3 | 1 |  | 0 | 1/3 | 2/3 | 1
X7 | People activity level computer lab | 100 | 140 | 150 |  | 100 | 116.67 | 133.33 | 150
X8 | People activity level offices | 100 | 140 | 150 |  | 100 | 116.67 | 133.33 | 150
X9 | People activity level lecture rooms | 100 | 140 | 150 |  | 100 | 116.67 | 133.33 | 150
X10 | Light fraction radiant | 0 | 0.27 | 1 |  | 0 | 1/3 | 2/3 | 1
X11 | Equipment fraction radiant | 0 | 0 | 1 |  | 0 | 1/3 | 2/3 | 1
X12 | Air Infiltration airchanges/hour | 0.1 | 1 | 6 |  | 0.1 | 2.06667 | 4.0333 | 6
X13 | Fan total efficiency | 0.3 | 0.6 | 0.9 |  | .3 | .5 | .7 | .9
X14 | Pressure rise | 30 | 75 | 120 |  | 30 | 60 | 90 | 120
X15 | DXCoolingCoil COP | 1 | 2.7 | 5 |  | 1 | 2.3333 | 3.66667 | 5
DISCRETE PARAMETERS
| No. of people schedule |  |  |  | IRM
| Setpoint schedule |  |  |  | Manually tuned
| Auxiliary equipment |  |  |  | Building Audit
| Equipment schedule |  |  |  | IRM
| Lighting schedule |  |  |  | IRM
x* = {2/3, 2/3, 2/3, 0, 2/3, 0, 2/3, 1/3, 1/3, 0, 1/3, 2/3, 0, 2/3, 2/3}

## Sheet2
Column1 | X1 | X2 | X3 | X4 | X5 | X6 | X7 | X8 | X9 | X10 | X11 | X12 | X13 | X14 | X15
1 | 0.001 | 0 | 0.33367 | 0.66667 | 0.334 | 0.33333 | 116.6667 | 100 | 133.3333 | 0.33333 | 0.66667 | 2.0667 | 0.9 | 90 | 2.3333
2 | 0.001 | 0 | 0.33367 | 1 | 0.334 | 0.33333 | 116.6667 | 100 | 133.3333 | 0.33333 | 0.66667 | 2.0667 | 0.9 | 90 | 2.3333
3 | 0.001 | 0 | 0.33367 | 1 | 0.334 | 0.33333 | 116.6667 | 100 | 133.3333 | 0.33333 | 0.33333 | 2.0667 | 0.9 | 90 | 2.3333
4 | 0.001 | 0 | 0.33367 | 1 | 0.334 | 0.33333 | 116.6667 | 100 | 133.3333 | 0.33333 | 0.33333 | 2.0667 | 0.7 | 90 | 2.3333
5 | 0.33367 | 0 | 0.33367 | 1 | 0.334 | 0.33333 | 116.6667 | 100 | 133.3333 | 0.33333 | 0.33333 | 2.0667 | 0.7 | 90 | 2.3333
6 | 0.33367 | 0 | 0.33367 | 1 | 0.334 | 0.33333 | 116.6667 | 100 | 133.3333 | 0.66667 | 0.33333 | 2.0667 | 0.7 | 90 | 2.3333
7 | 0.33367 | 0 | 0.33367 | 1 | 0.334 | 0.33333 | 116.6667 | 100 | 133.3333 | 0.66667 | 0.33333 | 2.0667 | 0.7 | 60 | 2.3333
8 | 0.33367 | 0 | 0.33367 | 1 | 0.334 | 0.66667 | 116.6667 | 100 | 133.3333 | 0.66667 | 0.33333 | 2.0667 | 0.7 | 60 | 2.3333
9 | 0.33367 | 0 | 0.33367 | 1 | 0.334 | 0.66667 | 116.6667 | 100 | 133.3333 | 0.66667 | 0.33333 | 0.1 | 0.7 | 60 | 2.3333
10 | 0.33367 | 0 | 0.33367 | 1 | 0.334 | 0.66667 | 100 | 100 | 133.3333 | 0.66667 | 0.33333 | 0.1 | 0.7 | 60 | 2.3333
11 | 0.33367 | 0.33333 | 0.33367 | 1 | 0.334 | 0.66667 | 100 | 100 | 133.3333 | 0.66667 | 0.33333 | 0.1 | 0.7 | 60 | 2.3333
12 | 0.33367 | 0.33333 | 0.33367 | 1 | 0.334 | 0.66667 | 100 | 100 | 150 | 0.66667 | 0.33333 | 0.1 | 0.7 | 60 | 2.3333
13 | 0.33367 | 0.33333 | 0.33367 | 1 | 0.334 | 0.66667 | 100 | 116.6667 | 150 | 0.66667 | 0.33333 | 0.1 | 0.7 | 60 | 2.3333
14 | 0.33367 | 0.33333 | 0.33367 | 1 | 0.334 | 0.66667 | 100 | 116.6667 | 150 | 0.66667 | 0.33333 | 0.1 | 0.7 | 60 | 1
15 | 0.33367 | 0.33333 | 0.33367 | 1 | 0.001 | 0.66667 | 100 | 116.6667 | 150 | 0.66667 | 0.33333 | 0.1 | 0.7 | 60 | 1
16 | 0.33367 | 0.33333 | 0.66633 | 1 | 0.001 | 0.66667 | 100 | 116.6667 | 150 | 0.66667 | 0.33333 | 0.1 | 0.7 | 60 | 1
17 | 0.66633 | 0.66667 | 0.66633 | 0.66667 | 0.667 | 1 | 100 | 133.3333 | 116.6667 | 0.66667 | 0.66667 | 2.0667 | 0.5 | 60 | 5
18 | 0.66633 | 0.66667 | 0.66633 | 0.66667 | 0.667 | 1 | 100 | 133.3333 | 100 | 0.66667 | 0.66667 | 2.0667 | 0.5 | 60 | 5
19 | 0.66633 | 1 | 0.66633 | 0.66667 | 0.667 | 1 | 100 | 133.3333 | 100 | 0.66667 | 0.66667 | 2.0667 | 0.5 | 60 | 5
20 | 0.66633 | 1 | 0.66633 | 0.66667 | 0.667 | 1 | 116.6667 | 133.3333 | 100 | 0.66667 | 0.66667 | 2.0667 | 0.5 | 60 | 5
21 | 0.66633 | 1 | 0.66633 | 0.66667 | 0.667 | 1 | 116.6667 | 133.3333 | 100 | 0.66667 | 0.66667 | 4.0333 | 0.5 | 60 | 5
22 | 0.66633 | 1 | 0.66633 | 0.66667 | 0.667 | 1 | 116.6667 | 133.3333 | 100 | 0.66667 | 0.66667 | 4.0333 | 0.5 | 60 | 3.6667
23 | 0.66633 | 1 | 0.66633 | 1 | 0.667 | 1 | 116.6667 | 133.3333 | 100 | 0.66667 | 0.66667 | 4.0333 | 0.5 | 60 | 3.6667
24 | 0.66633 | 1 | 0.66633 | 1 | 0.667 | 1 | 116.6667 | 133.3333 | 100 | 0.66667 | 0.66667 | 4.0333 | 0.5 | 90 | 3.6667
25 | 0.66633 | 1 | 0.66633 | 1 | 0.667 | 1 | 116.6667 | 133.3333 | 100 | 0.66667 | 0.33333 | 4.0333 | 0.5 | 90 | 3.6667
26 | 0.66633 | 1 | 0.999 | 1 | 0.667 | 1 | 116.6667 | 133.3333 | 100 | 0.66667 | 0.33333 | 4.0333 | 0.5 | 90 | 3.6667
27 | 0.66633 | 1 | 0.999 | 1 | 0.667 | 1 | 116.6667 | 133.3333 | 100 | 1 | 0.33333 | 4.0333 | 0.5 | 90 | 3.6667
28 | 0.66633 | 1 | 0.999 | 1 | 0.667 | 0.66667 | 116.6667 | 133.3333 | 100 | 1 | 0.33333 | 4.0333 | 0.5 | 90 | 3.6667
29 | 0.33367 | 1 | 0.999 | 1 | 0.667 | 0.66667 | 116.6667 | 133.3333 | 100 | 1 | 0.33333 | 4.0333 | 0.5 | 90 | 3.6667
30 | 0.33367 | 1 | 0.999 | 1 | 0.667 | 0.66667 | 116.6667 | 116.6667 | 100 | 1 | 0.33333 | 4.0333 | 0.5 | 90 | 3.6667
31 | 0.33367 | 1 | 0.999 | 1 | 1 | 0.66667 | 116.6667 | 116.6667 | 100 | 1 | 0.33333 | 4.0333 | 0.5 | 90 | 3.6667
32 | 0.33367 | 1 | 0.999 | 1 | 1 | 0.66667 | 116.6667 | 116.6667 | 100 | 1 | 0.33333 | 4.0333 | 0.3 | 90 | 3.6667
33 | 0.66633 | 0.33333 | 0.999 | 0.33333 | 0.001 | 1 | 100 | 100 | 150 | 0.33333 | 0.66667 | 2.0667 | 0.5 | 90 | 3.6667
34 | 0.66633 | 0.33333 | 0.999 | 0.33333 | 0.001 | 1 | 100 | 100 | 150 | 0.33333 | 1 | 2.0667 | 0.5 | 90 | 3.6667
35 | 0.66633 | 0.33333 | 0.999 | 0.33333 | 0.001 | 1 | 116.6667 | 100 | 150 | 0.33333 | 1 | 2.0667 | 0.5 | 90 | 3.6667
36 | 0.66633 | 0.33333 | 0.999 | 0.66667 | 0.001 | 1 | 116.6667 | 100 | 150 | 0.33333 | 1 | 2.0667 | 0.5 | 90 | 3.6667
37 | 0.66633 | 0.33333 | 0.999 | 0.66667 | 0.001 | 1 | 116.6667 | 100 | 150 | 0.33333 | 1 | 0.1 | 0.5 | 90 | 3.6667
38 | 0.66633 | 0.33333 | 0.66633 | 0.66667 | 0.001 | 1 | 116.6667 | 100 | 150 | 0.33333 | 1 | 0.1 | 0.5 | 90 | 3.6667
39 | 0.33367 | 0.33333 | 0.66633 | 0.66667 | 0.001 | 1 | 116.6667 | 100 | 150 | 0.33333 | 1 | 0.1 | 0.5 | 90 | 3.6667
40 | 0.33367 | 0.33333 | 0.66633 | 0.66667 | 0.001 | 1 | 116.6667 | 100 | 150 | 0.33333 | 1 | 0.1 | 0.5 | 120 | 3.6667
41 | 0.33367 | 0.33333 | 0.66633 | 0.66667 | 0.001 | 1 | 116.6667 | 100 | 150 | 0 | 1 | 0.1 | 0.5 | 120 | 3.6667
42 | 0.33367 | 0.33333 | 0.66633 | 0.66667 | 0.001 | 1 | 116.6667 | 100 | 150 | 0 | 1 | 0.1 | 0.5 | 120 | 2.3333
43 | 0.33367 | 0.33333 | 0.66633 | 0.66667 | 0.001 | 1 | 116.6667 | 100 | 133.3333 | 0 | 1 | 0.1 | 0.5 | 120 | 2.3333
44 | 0.33367 | 0.33333 | 0.66633 | 0.66667 | 0.001 | 0.66667 | 116.6667 | 100 | 133.3333 | 0 | 1 | 0.1 | 0.5 | 120 | 2.3333
45 | 0.33367 | 0.66667 | 0.66633 | 0.66667 | 0.001 | 0.66667 | 116.6667 | 100 | 133.3333 | 0 | 1 | 0.1 | 0.5 | 120 | 2.3333
46 | 0.33367 | 0.66667 | 0.66633 | 0.66667 | 0.001 | 0.66667 | 116.6667 | 100 | 133.3333 | 0 | 1 | 0.1 | 0.3 | 120 | 2.3333
47 | 0.33367 | 0.66667 | 0.66633 | 0.66667 | 0.001 | 0.66667 | 116.6667 | 116.6667 | 133.3333 | 0 | 1 | 0.1 | 0.3 | 120 | 2.3333
48 | 0.33367 | 0.66667 | 0.66633 | 0.66667 | 0.334 | 0.66667 | 116.6667 | 116.6667 | 133.3333 | 0 | 1 | 0.1 | 0.3 | 120 | 2.3333
49 | 0.001 | 0.66667 | 0.66633 | 0.66667 | 0.667 | 0 | 133.3333 | 133.3333 | 133.3333 | 0.66667 | 1 | 2.0667 | 0.5 | 90 | 5
50 | 0.001 | 0.66667 | 0.66633 | 0.66667 | 0.334 | 0 | 133.3333 | 133.3333 | 133.3333 | 0.66667 | 1 | 2.0667 | 0.5 | 90 | 5
51 | 0.001 | 0.66667 | 0.66633 | 0.66667 | 0.334 | 0 | 133.3333 | 133.3333 | 133.3333 | 0.66667 | 1 | 2.0667 | 0.5 | 120 | 5
52 | 0.001 | 0.66667 | 0.66633 | 0.66667 | 0.334 | 0.33333 | 133.3333 | 133.3333 | 133.3333 | 0.66667 | 1 | 2.0667 | 0.5 | 120 | 5
53 | 0.001 | 0.66667 | 0.66633 | 0.66667 | 0.334 | 0.33333 | 133.3333 | 133.3333 | 133.3333 | 0.66667 | 1 | 0.1 | 0.5 | 120 | 5
54 | 0.001 | 0.66667 | 0.66633 | 0.66667 | 0.334 | 0.33333 | 133.3333 | 133.3333 | 133.3333 | 0.66667 | 1 | 0.1 | 0.5 | 120 | 3.6667
55 | 0.001 | 0.66667 | 0.66633 | 0.66667 | 0.334 | 0.33333 | 133.3333 | 133.3333 | 133.3333 | 0.33333 | 1 | 0.1 | 0.5 | 120 | 3.6667
56 | 0.001 | 1 | 0.66633 | 0.66667 | 0.334 | 0.33333 | 133.3333 | 133.3333 | 133.3333 | 0.33333 | 1 | 0.1 | 0.5 | 120 | 3.6667
57 | 0.001 | 1 | 0.66633 | 0.66667 | 0.334 | 0.33333 | 133.3333 | 133.3333 | 133.3333 | 0.33333 | 1 | 0.1 | 0.7 | 120 | 3.6667
58 | 0.001 | 1 | 0.66633 | 0.66667 | 0.334 | 0.33333 | 133.3333 | 133.3333 | 150 | 0.33333 | 1 | 0.1 | 0.7 | 120 | 3.6667
59 | 0.001 | 1 | 0.66633 | 0.66667 | 0.334 | 0.33333 | 133.3333 | 133.3333 | 150 | 0.33333 | 0.66667 | 0.1 | 0.7 | 120 | 3.6667
60 | 0.001 | 1 | 0.999 | 0.66667 | 0.334 | 0.33333 | 133.3333 | 133.3333 | 150 | 0.33333 | 0.66667 | 0.1 | 0.7 | 120 | 3.6667
61 | 0.001 | 1 | 0.999 | 0.66667 | 0.334 | 0.33333 | 133.3333 | 150 | 150 | 0.33333 | 0.66667 | 0.1 | 0.7 | 120 | 3.6667
62 | 0.001 | 1 | 0.999 | 0.66667 | 0.334 | 0.33333 | 150 | 150 | 150 | 0.33333 | 0.66667 | 0.1 | 0.7 | 120 | 3.6667
63 | 0.001 | 1 | 0.999 | 1 | 0.334 | 0.33333 | 150 | 150 | 150 | 0.33333 | 0.66667 | 0.1 | 0.7 | 120 | 3.6667
64 | 0.33367 | 1 | 0.999 | 1 | 0.334 | 0.33333 | 150 | 150 | 150 | 0.33333 | 0.66667 | 0.1 | 0.7 | 120 | 3.6667
65 | 0.66633 | 0.66667 | 0.33367 | 1 | 0.667 | 0.66667 | 150 | 100 | 133.3333 | 0.66667 | 0.33333 | 2.0667 | 0.7 | 60 | 3.6667
66 | 0.66633 | 0.66667 | 0.33367 | 0.66667 | 0.667 | 0.66667 | 150 | 100 | 133.3333 | 0.66667 | 0.33333 | 2.0667 | 0.7 | 60 | 3.6667
67 | 0.66633 | 0.66667 | 0.33367 | 0.66667 | 0.667 | 0.66667 | 150 | 100 | 133.3333 | 0.66667 | 0.33333 | 4.0333 | 0.7 | 60 | 3.6667
68 | 0.66633 | 0.66667 | 0.001 | 0.66667 | 0.667 | 0.66667 | 150 | 100 | 133.3333 | 0.66667 | 0.33333 | 4.0333 | 0.7 | 60 | 3.6667
69 | 0.66633 | 0.66667 | 0.001 | 0.66667 | 0.667 | 0.66667 | 150 | 100 | 133.3333 | 1 | 0.33333 | 4.0333 | 0.7 | 60 | 3.6667
70 | 0.66633 | 1 | 0.001 | 0.66667 | 0.667 | 0.66667 | 150 | 100 | 133.3333 | 1 | 0.33333 | 4.0333 | 0.7 | 60 | 3.6667
71 | 0.66633 | 1 | 0.001 | 0.66667 | 0.667 | 0.66667 | 150 | 100 | 133.3333 | 1 | 0.33333 | 4.0333 | 0.7 | 60 | 5
72 | 0.66633 | 1 | 0.001 | 0.66667 | 1 | 0.66667 | 150 | 100 | 133.3333 | 1 | 0.33333 | 4.0333 | 0.7 | 60 | 5
73 | 0.66633 | 1 | 0.001 | 0.66667 | 1 | 0.66667 | 150 | 100 | 116.6667 | 1 | 0.33333 | 4.0333 | 0.7 | 60 | 5
74 | 0.999 | 1 | 0.001 | 0.66667 | 1 | 0.66667 | 150 | 100 | 116.6667 | 1 | 0.33333 | 4.0333 | 0.7 | 60 | 5
75 | 0.999 | 1 | 0.001 | 0.66667 | 1 | 0.66667 | 150 | 100 | 116.6667 | 1 | 0.33333 | 4.0333 | 0.5 | 60 | 5
76 | 0.999 | 1 | 0.001 | 0.66667 | 1 | 1 | 150 | 100 | 116.6667 | 1 | 0.33333 | 4.0333 | 0.5 | 60 | 5
77 | 0.999 | 1 | 0.001 | 0.66667 | 1 | 1 | 150 | 116.6667 | 116.6667 | 1 | 0.33333 | 4.0333 | 0.5 | 60 | 5
78 | 0.999 | 1 | 0.001 | 0.66667 | 1 | 1 | 150 | 116.6667 | 116.6667 | 1 | 0.66667 | 4.0333 | 0.5 | 60 | 5
79 | 0.999 | 1 | 0.001 | 0.66667 | 1 | 1 | 133.3333 | 116.6667 | 116.6667 | 1 | 0.66667 | 4.0333 | 0.5 | 60 | 5
80 | 0.999 | 1 | 0.001 | 0.66667 | 1 | 1 | 133.3333 | 116.6667 | 116.6667 | 1 | 0.66667 | 4.0333 | 0.5 | 30 | 5